## Residential
Hour | Occupancy | Equipment | Light | Ventilation | T_set_winter | T_set_summer | People_activity [W/person] | People_density [person/m2] | Electric_equipment [W/m2] | Lighting_level [W/m2]
0 | 0.7 | 0.1 | 0.1 | 0.4 | 17 | 25 | 120 | 0.04 | 4 | 9
1 | 0.7 | 0.1 | 0.1 | 0.4 | 17 | 25 | ISO 7730 / ISO 8996 | DIN EN 16798-1 + DIN EN 15232 | VDI 2067 Blatt 1 | EN 12464-1 (Indoor Lighting - Illuminance Standard) + DIN V 18599-4 (Lighting energy consumption)
2 | 0.7 | 0.1 | 0.1 | 0.4 | 17 | 25 | https://www.iso.org |  | https://www.vdi.de
3 | 0.7 | 0.1 | 0.1 | 0.4 | 17 | 25
4 | 0.7 | 0.1 | 0.1 | 0.4 | 20 | 25
5 | 0.7 | 0.1 | 0.1 | 0.4 | 21 | 26 |  | n_air_infiltration [1/h]
6 | 1 | 0.4 | 0.5 | 0.4 | 21 | 26 |  | 0.1-0.3
7 | 1 | 0.4 | 0.5 | 0.4 | 21 | 26 |  | DIN 4108-2
8 | 1 | 0.1 | 0.05 | 0.4 | 21 | 26 |  | https://www.din.de
9 | 0.2 | 0.1 | 0.05 | 0.4 | 21 | 26
10 | 0.2 | 0.1 | 0.05 | 0.4 | 21 | 26
11 | 0.2 | 0.1 | 0.05 | 0.4 | 21 | 26
12 | 0.2 | 0.1 | 0.05 | 0.4 | 21 | 26
13 | 0.2 | 0.1 | 0.05 | 0.4 | 21 | 26
14 | 0.2 | 0.1 | 0.05 | 0.4 | 21 | 26
15 | 0.2 | 0.1 | 0.05 | 0.4 | 21 | 26
16 | 0.6 | 1 | 1 | 0.4 | 21 | 26
17 | 1 | 1 | 1 | 0.4 | 21 | 26
18 | 1 | 1 | 1 | 0.4 | 21 | 26
19 | 1 | 1 | 1 | 0.4 | 21 | 26
20 | 1 | 1 | 1 | 0.4 | 21 | 26
21 | 1 | 1 | 1 | 0.4 | 21 | 26
22 | 0.8 | 0.2 | 0.2 | 0.4 | 20 | 25
23 | 0.8 | 0.2 | 0.2 | 0.4 | 17 | 25
| DIN EN 16798-1 |  |  | DIN 1946-6 | DIN EN 16798-1 + DIN EN ISO 13790 | DIN EN 16798-1 + DIN EN ISO 13790
| https://www.dena.de |  |  | https://www.din.de | https://www.iso.org | https://www.iso.org
https://www.tab.de

## School
Hour | Occupancy | Equipment | Light | Ventilation | T_set_winter_wd | T_set_winter_we | T_set_summer | People_activity [W/person] | People_density [person/m2] | Electric_equipment [W/m2] | Lighting_level [W/m2]
0 | 0 | 0 | 0 | 0.1 | 20 | 18 | 26 | 120 | 0.2 | 10 | 15
1 | 0 | 0 | 0 | 0.1 | 20 | 18 | 26 | ISO 7730 / ISO 8996 | DIN EN 16798-1 + DIN EN 15232 | CIBSE Guide A | EN 12464-1 (Indoor Lighting - Illuminance Standard) + DIN V 18599-4 (Lighting energy consumption)
2 | 0 | 0 | 0 | 0.1 | 20 | 18 | 26 | https://www.iso.org |  | https://www.cibse.org
3 | 0 | 0 | 0 | 0.1 | 20 | 18 | 26
4 | 0 | 0 | 0 | 0.1 | 20 | 18 | 26
5 | 0 | 0 | 0 | 0.1 | 20 | 18 | 26
6 | 0 | 0 | 0 | 0.1 | 20 | 18 | 26
7 | 0.5 | 0.4 | 0.3 | 1 | 20 | 18 | 26
8 | 0.5 | 0.4 | 0.3 | 1.1 | 20 | 18 | 26
9 | 1 | 1 | 1 | 1.2 | 20 | 18 | 26
10 | 1 | 1 | 1 | 1.3 | 20 | 18 | 26
11 | 1 | 1 | 1 | 1.4 | 20 | 18 | 26
12 | 1 | 1 | 1 | 1.5 | 20 | 18 | 26
13 | 1 | 1 | 1 | 1.5 | 20 | 18 | 26
14 | 1 | 1 | 1 | 1.4 | 20 | 18 | 26
15 | 1 | 1 | 1 | 1.3 | 20 | 18 | 26
16 | 1 | 1 | 1 | 1.2 | 20 | 18 | 26
17 | 0.3 | 0.2 | 0.2 | 1.1 | 20 | 18 | 26
18 | 0.3 | 0.2 | 0.2 | 1 | 20 | 18 | 26
19 | 0.3 | 0.2 | 0.2 | 0.1 | 20 | 18 | 26
20 | 0 | 0 | 0 | 0.1 | 20 | 18 | 26
21 | 0 | 0 | 0 | 0.1 | 20 | 18 | 26
22 | 0 | 0 | 0 | 0.1 | 20 | 18 | 26
23 | 0 | 0 | 0 | 0.1 | 20 | 18 | 26
| DIN EN ISO 13790 + DIN EN 16798-1 (occupancy schedules) |  |  | DIN EN 16798-3 | DIN EN 16798-1 + DIN EN ISO 13790 | DIN EN 16798-1 + DIN EN ISO 13790 | DIN EN 16798-1 + DIN EN ISO 13790
| https://www.dena.de |  |  |  | https://www.iso.org | https://www.iso.org | https://www.iso.org

## Office
Hour | Occupancy | Equipment | Light | Ventilation | T_set_winter_wd | T_set_winter_we | T_set_summer | People_activity [W/person] | People_density [person/m2] | Electric_equipment [W/m2] | Lighting_level [W/m2]
0 | 0 | 0 | 0 | 0.1 | 20 | 18 | 26 | 120 | 0.1 | 13 | 15
1 | 0 | 0 | 0 | 0.1 | 20 | 18 | 26 | ISO 7730 / ISO 8996 | DIN EN 16798-1 + DIN EN 15232 | CIBSE Guide A | EN 12464-1 (Indoor Lighting - Illuminance Standard) + DIN V 18599-4 (Lighting energy consumption)
2 | 0 | 0 | 0 | 0.1 | 20 | 18 | 26 | https://www.iso.org |  | https://www.cibse.org
3 | 0 | 0 | 0 | 0.1 | 20 | 18 | 26
4 | 0 | 0 | 0 | 0.1 | 20 | 18 | 26
5 | 0 | 0 | 0 | 0.1 | 20 | 18 | 26
6 | 0 | 0 | 0 | 0.1 | 20 | 18 | 26
7 | 0.5 | 0.4 | 0.3 | 1 | 20 | 18 | 26
8 | 0.5 | 0.4 | 0.3 | 1.1 | 20 | 18 | 26
9 | 1 | 1 | 1 | 1.2 | 20 | 18 | 26
10 | 1 | 1 | 1 | 1.3 | 20 | 18 | 26
11 | 1 | 1 | 1 | 1.4 | 20 | 18 | 26
12 | 1 | 1 | 1 | 1.5 | 20 | 18 | 26
13 | 1 | 1 | 1 | 1.5 | 20 | 18 | 26
14 | 1 | 1 | 1 | 1.4 | 20 | 18 | 26
15 | 1 | 1 | 1 | 1.3 | 20 | 18 | 26
16 | 1 | 1 | 1 | 1.2 | 20 | 18 | 26
17 | 0.3 | 0.2 | 0.2 | 1.1 | 20 | 18 | 26
18 | 0.3 | 0.2 | 0.2 | 1 | 20 | 18 | 26
19 | 0.3 | 0.2 | 0.2 | 0.1 | 20 | 18 | 26
20 | 0 | 0 | 0 | 0.1 | 20 | 18 | 26
21 | 0 | 0 | 0 | 0.1 | 20 | 18 | 26
22 | 0 | 0 | 0 | 0.1 | 20 | 18 | 26
23 | 0 | 0 | 0 | 0.1 | 20 | 18 | 26
| DIN EN ISO 13790 + DIN EN 16798-1 (occupancy schedules) |  |  | DIN EN 16798-3 | DIN EN 16798-1 + DIN EN ISO 13790 | DIN EN 16798-1 + DIN EN ISO 13790 | DIN EN 16798-1 + DIN EN ISO 13790
| https://www.dena.de |  |  |  | https://www.iso.org | https://www.iso.org | https://www.iso.org

## Commercial
Hour | Occupancy | Equipment | Light | Ventilation | T_set_winter_workingTime | T_set_summer_workingTime | People_activity [W/person] | People_density [person/m2] | Electric_equipment [W/m2] | Lighting_level [W/m2]
0 | 0 | 0.05 | 0 | 0.1 | 16 | 28 | 120 | 0.2 | 10 | 15
1 | 0 | 0.05 | 0 | 0.1 | 16 | 28 | ISO 7730 / ISO 8996 | DIN EN 16798-1 + DIN EN 15232 | CIBSE Guide A | EN 12464-1 (Indoor Lighting - Illuminance Standard) + DIN V 18599-4 (Lighting energy consumption)
2 | 0 | 0.05 | 0 | 0.1 | 16 | 28 | https://www.iso.org |  | https://www.cibse.org
3 | 0 | 0.05 | 0 | 0.1 | 16 | 28
4 | 0 | 0.05 | 0 | 0.1 | 16 | 28 | Working Hour
5 | 0 | 0.1 | 0.1 | 0.2 | 19 | 27 | 08:00 - 20:00
6 | 0.05 | 0.2 | 0.2 | 0.3 | 19 | 27 | DIN V 18599-10
7 | 0.1 | 0.3 | 0.5 | 0.5 | 19 | 27
8 | 0.3 | 0.6 | 1 | 1.5 | 20 | 26
9 | 0.6 | 0.8 | 1 | 1.8 | 20 | 26
10 | 0.7 | 1 | 1 | 2 | 20 | 26
11 | 0.8 | 1 | 1 | 2 | 20 | 26
12 | 1 | 1 | 1 | 2 | 20 | 26
13 | 1 | 1 | 1 | 2 | 20 | 26
14 | 1 | 1 | 1 | 2 | 20 | 26
15 | 0.9 | 1 | 1 | 2 | 20 | 26
16 | 0.8 | 1 | 1 | 2 | 20 | 26
17 | 0.7 | 0.8 | 1 | 1.8 | 20 | 26
18 | 0.5 | 0.6 | 0.8 | 1.5 | 19 | 26
19 | 0.3 | 0.4 | 0.5 | 1 | 19 | 27
20 | 0.1 | 0.2 | 0.2 | 0.5 | 18 | 27
21 | 0.05 | 0.1 | 0.1 | 0.2 | 17 | 28
22 | 0 | 0.05 | 0 | 0.1 | 16 | 28
23 | 0 | 0.05 | 0 | 0.1 | 16 | 28
| DIN EN ISO 13790 + DIN EN 16798-1 (occupancy schedules) |  |  | DIN EN 16798-3 | DIN EN 16798-1 + DIN EN ISO 13790 | DIN EN 16798-1 + DIN EN ISO 13790
| https://www.dena.de |  |  |  | https://www.iso.org | https://www.iso.org